# Validation Report

This is an example of the validation report that is to be submitted by developers. Example of the validation procedure will be outlined for the IEEE Type ST1A excitation system.

# Model Description

The model description originates from the IEEE document and it is presented in the following text.

The computer model of the Type ST1A potential-source controlled-rectifier excitation system shown in Figure 1 is intended to represent systems in which excitation power is supplied through a transformer from the generator terminals (or the unit’s auxiliary bus) and is regulated by a controlled rectifier. The maximum exciter voltage available from such systems is directly related to the generator terminal voltage (except as noted, as follows).

In this type of system, the inherent exciter time constants are very small, and exciter stabilization may not be required. On the other hand, it may be desirable to reduce the transient gain of these systems for other reasons. The model shown is sufficiently versatile to represent transient gain reduction implemented either in the forward path via time constants, TB and TC (in which case KF would normally be set to zero), or in the feedback path by suitable choice of rate feedback parameters, KF and TF. Voltage regulator gain and any inherent excitation system time constant are represented by KA and TA, respectively.

The time constants, TC1 and TB1, allow for the possibility of representing transient gain increase, in which case TC1 would be greater than TB1.

The way in which the firing angle for the bridge rectifiers is derived affects the input-output relationship, which is assumed to be linear in the model by choice of a simple gain, KA. For many systems a truly linear relationship applies. In a few systems, the bridge relationship is not linearized, leaving this nominally linear gain a sinusoidal function, the amplitude of which may be dependent on the supply voltage. As the gain is normally set very high, a linearization of this characteristic is normally satisfactory for modeling purposes. The representation of the ceiling is the same whether the characteristic is linear or sinusoidal.

In many cases, the internal limits on VI can be neglected. The field voltage limits that are functions of both terminal voltage and synchronous machine field current should be modeled. The representation of the field voltage positive limit as a linear function of synchronous machine field current is possible because operation of the rectifier bridge in such systems is confined to the mode 1 region. The negative limit would have a similar current-dependent characteristic, but the sign of the term could be either positive or negative depending upon whether a constant firing angle or constant extinction angle is chosen for the limit. As field current is normally low under this condition, the term is not included in the model.

As a result of the very high forcing capability of these systems, a field current limiter is sometimes employed to protect the generator rotor and exciter. The limit start setting is defined by ILR and the gain is represented by KLR. To permit this limit to be ignored, provision should be made to allow KLR to be set to zero. This limiter is described here to maintain consistency with the original ST1A model.

While for the majority of these excitation systems, a fully controlled bridge is employed, the model is also applicable to systems in which only half of the bridge is controlled, in which case the negative field voltage limit is set to zero (VRMIN = 0).

Figure 1 Block diagram of the excitation system model EXST1

# Model Validation

## Validation Model

To validate the model of the excitation system, simple Single Machine Infinite Bus (SMIB) system was built in Modelica (see Fig. 2a). The system contains one generator model (see Fig 2b) which includes the model of the round rotor machine and the excitation system model being validated, infinite bus, load, line and fault models.

- Generator model

- Model of the SMIB system

Figure 2 Modelica model used to validate the excitation system model

The same power system model was built in the PSS/E (see Fig. 3). Power flow results obtained with PSS/E were used to initialize the Modelica model from Fig. 2.

Figure 3 PSS/E model used as a reference during the validation procedure

The disturbance is applied to the system in order to excite its dynamics. Three phase fault to ground is introduced at the bus FAULT with the impedance of (0.1 + j0.1) pu in duration of 150ms. The fault is cleared by opening the lines adjacent to the bus where the fault was introduced.

## Simulation Parameters

PSS/E does not provide the same flexibility as Modelica does when it comes to the choice of supported solvers. It uses the second order Range Kutta integration method with a fixed time step. Thus, to avoid the solver related differences in the simulation results, the same solver was used to simulate the Modelica model. Some of the solver parameters are given in Table 1.

Table 1 Modelica and PSS/E solver parameters

| Solver |  | Runge Kutta 2 |  |
| --- | --- | --- | --- |
| Time step | 0.005 | Tolerance | 0.0001 |

## Simulation Results and Analysis

Upon the execution of the simulation, results are plotted and analysed. The analysed signals should, if possible, include the state variables of the model in question, but other relevant signals as well.

The both simulation results are shown in Fig. 4. Along with the actual signals, relative percentage error of the signal from Modelica with respect to the one from PSS/E is given for the particular time instants.

Figure 4 Comparison of the simulated models

In addition, validation of the model should be based on the quantitative assessment of the signals by using a root mean square error (RMSE) calculations. For each of the signals shown in Fig. 4, RMSE was calculated and shown Table 2.

Table 2 Calculated RMSE values

| Signal | Terminal voltage | Excitation voltage | Active power | Reactive power |
| --- | --- | --- | --- | --- |
| RMSE | 7.02∙10-5 | 3.82∙10-3 | 7.71∙10-5 | 1.76∙10-4 |

IEEE Recommended Practice for Excitation System Models for Power System Stability Studies, IEEE PES, IEEE Std 421.5-2005